## 3.1 Property_Contractor Details
3.1 Cooling Tower Water Management Plan (CTWMP) Template
This Cooling Tower Water Management Plan (CTWMP) template will assist you to detail the cooling tower systems
in place at your site as well as identify how these systems are being managed with regards to overall water
consumption and efficiency.
This CTWMP is to be complied with by all relevant parties, including property owners, managers and contractors.
Any non-compliance is to be immediately reported to the Principal.
Frequency of reporting and updating details in the plan are at the discretion of the owner.
Site and Contractor Details:
Date CTWMP completed: | 2017-06-01
Next Review date: | 2018-06-01
Site Details
Site Address | 111 Sydney Street, Sydney
Site Contact | Name | A. Smith
| Telephone | 02 9999 9999
| Email | a.smith@abc.com.au
| Position | Sustainability Manager
Contractor Details
Mechanical Services Contractor | Company name | XYZ Pty Ltd
| Contact | M.Smith
Water Treatment Contractor | Company name | FGH Pty Ltd
| Contact | J.Smith
Property Information:
Property Net Lettable Area (NLA) or/ | 25000
Property Gross Lettable Area (GLA)
Operating Days per Week | 5
Operating Hours per Day | 10
Cooling Tower Water Management Plan Team Members:
(it is recommended that a range of stakeholders are included in this process)
Name | Company/Department |  | Role
B. Smith | ABC Pty Ltd |  | Sustainability Manager
C.Smith | XYZ Pty Ltd |  | Contract Manager
J.Smith | FGH Pty Ltd |  | Contract Manager

## 3.2 Water Charge Details
3.2 Water Charge Details
Documenting and understanding water and wastewater charge details is a very important step
in a comprehensive cooling tower water management plan.
The costs of operating a cooling tower system from a water consumption perspective can be significant
and understanding the impact that water conservation initiatives have on overall property costs
should be evaluated and understood.
(Note:Input data into the orange shaded cells to facilitate automatic calculations)
Cooling Tower Water Charge Details:
Charge Type | Previous 12 months
Total Property Water Consumption (kL) | 15000
Total Cooling Tower Water Consumption (kL) | 5000
Cooling Tower Water Consumption - % of Total (%) | 33.33%
Water Usage Charge Rate ($/kL) | 2.2
Wastewater Usage Charge Rate ($/kL) | 1.1
Sewer Usage Discharge Factor (%) | 90%
Total Water Charge Rate ($/kL) | 3.19
Cooling Tower Water Charge Cost ($/yr) | 11000
Cooling Tower Wastewater Charge Cost ($/yr) | 4950
Total Cooling Tower Water Charge Costs ($/yr) | 15950
Total Property Water Charge Costs ($/yr) | 47850
Note: These costs are estimates only and do not include any other fixed charges included in the
relevant water authority bills.
Should be used for indication purposes only.

## 3.3 Technical Information
3.3 Cooling Tower System Details
The documentation and understanding of existing cooling tower systems on a property is an important part of managing cooling tower assets
and understanding system performance.
The table below provides a detailed summation of each cooling tower system and its design and operating details.
Cooling Tower Systems Technical Information:
Description | Details
| System No.1 | System No.2 | System No.3
System Identification | Main System
Cooling Towers (No of.) | 2
Cooling Towers (Make) | Aqua-Cool
Cooling Towers (Model No.) | AFT 8515
Cooling Towers (Type) | Induced draught cross flow
Location | Level 23
Equipment served by Towers | 1 x Carrier Centrifugal Chiller
Typical Hours of Operation | 12 hours/day: Mon-Fri
Design Water Flow - per Tower (l/s) | 82.5
Design Water Flow - System (l/s) | 165
Design Heat Rejection - per Tower (kW) | 1900
Design Heat Rejection - System (kW) | 3800
System Volume (m3) - estimated | 30000
Bleed Conductivity Setpoint (us/cm): | 1700

## 3.4 Water Consumption Tracking
3.4 Cooling Tower Water Efficiency Evaluation
Documenting and understanding historical cooling tower water consumption is a vital component of a best practice water efficiency program.
Understanding and tracking cooling tower water consumption trends, both historical and current, allows better overall monitoring and control.
This table allows a basic overview of cooling tower water consumption to be monitored and evaluated to ensure a basic level of understanding.
Site Name:
Description | Details
| System No.1 |  | System No.2 |  | System No.3
System Identification | Tenant System |  | Main System
Water Meter Identification Number | ABC 12345 |  | ABC 54321
Historical Water Consumption:
Cooling Tower Water Consumption | Previous Year (kL) | Current Year (kL) | Previous Year (kL) | Current Year (kL) | Previous Year (kL) | Current Year (kL)
January | 630 | 530 | 1260 | 1100 |  |  | 630 | 530 | 1260 | 1100
February | 700.3448 | 600 | 1400 | 1200 |  |  | 1330.3448 | 1130 | 2660 | 2300
March | 666.7742 | 567 | 1350 | 1160 |  |  | 1997.119 | 1697 | 4010 | 3460
April | 456.76 | 357 | 900 | 1400 |  |  | 2453.879 | 2054 | 4910 | 4860
May | 322.8387 | 232 | 650 | 1500 |  |  | 2776.7177 | 2286 | 5560 | 6360
June | 204 | 100 | 400 | 400 |  |  | 2980.7177 | 2386 | 5960 | 6760
July | 181.2065 | 120 | 360 | 400 |  |  | 3161.9243 | 2506 | 6320 | 7160
August | 198.9474 | 400 | 400 | 800 |  |  | 3360.8716 | 2906 | 6720 | 7960
September | 242.3281 |  | 500 |  |  |  | 3603.1997 |  | 7220
October | 267.5596 |  | 520 |  |  |  | 3870.7593 |  | 7740
November | 362.5652 |  | 720 |  |  |  | 4233.3245 |  | 8460
December | 315 |  | 630 |  |  |  | 4548.3245 |  | 9090
TOTAL | 4548.3245 | 2906 | 9090 | 7960 |  |  | 34947.1823 | 15495 |  | 39960
Average Monthly Water Consumption (kL/month) | 379.027 | 363.25 | 757.5 | 995
Average Daily Water Consumption (kL/day) | 12.4612 | 7.9616 | 24.9041 | 21.8082

## 3.5 Efficiency Calculations
3.5 Cooling Tower Water Consumption Evaluation
Undertaking regular evaluations of cooling tower water efficiency is a good way of understanding system operation.
This spreadsheet allows the regular evaluation of cooling tower water consumption against optimal water consumption based upon average monthly operating data.
Continuous monitoring of cooling tower water efficiency is recommended. However, those systems that do not have online monitoring systems can utilise this spreadsheet for reporting purposes.
Please note that is a simplified evaluation and does not take into account impact of system heat load variations.
| Month | Total Building Water Usage (kL) | Cooling Tower Water Usage (kL) | Cooling Tower Usage as a % of Building Usage | Average Daily Peak Temp. (°C) | Makeup Water EC (µS/cm) | Average System EC (µS/cm) | EC Set Point (µS/cm) | System Cycles | Set Point Cycles | Optimal Cycles (1700 µS/cm Upper Limit) | Estimated Blowdown (kL) | Estimated Evaporation (kL) | Optimal Water Usage (kL) | Excess Water Usage (kL) | Excess Water Usage %
| 2016-01-01 | 957 | 337 | 35.21% | 25.2 | 170 | 1650 | 1700 | 9.7059 | 10 | 10.2941 | 34.7212 | 302.2788 | 334.8025 | 2.1975 | 0.6564%
| 2016-02-01 | 988 | 307 | 31.07% | 31 | 170 | 1400 | 1700 | 8.2353 | 10 | 10.2941 | 37.2786 | 269.7214 | 298.7421 | 8.2579 | 2.764%
| 2016-03-01 | 998 | 300 | 30.06% | 28.7 | 170 | 1200 | 1700 | 7.0588 | 10 | 10.2941 | 42.5 | 257.5 | 285.2057 | 14.7943 | 5.187%
| 2016-04-01 | 865 | 195 | 22.54% | 26.7 | 170 | 1100 | 1700 | 6.4706 | 10 | 10.2941 | 30.1364 | 164.8636 | 182.6021 | 12.3979 | 6.79%
2016-05-01
2016-06-01
2016-07-01
2016-08-01
2016-09-01
2016-10-01
2016-11-01
2016-12-01
| Total/Average | 3808 | 1139 | 29.72% | 27.9 | 170 | 1337.5 | 1700 | 7.8676 | 10 | 10.2941 | 144.6361 | 994.3639 | 1101.3524 | 37.6476 | 3.418%
The following information should be inputted into the relevant columns to enable a complete analysis to be undertaken.
| Step 1: | Insert 'Monthly' building water consumption values (kL) into cells C9-C20
| Step 2: | Insert 'Monthly' cooling tower water consumption values (kL) into cells D9-D20
| Step 3: | Insert 'Average Daily Peak Temperature' into cells E9-E20 as taken from Bureau of Meterology Data or site data.
| Step 4: | Insert 'Makeup Water Electrical Conductivity' into cells F9-F20 as taken from Sydney Water Data or from water treatment sevice reports.
| Step 5: | Insert 'Average System Electrical Conductivity' into cells G9-G20 as taken from water treatment sevice reports. An average value is recommended if multiple values are available
| Step 6: | Insert 'Electrical Conductivity (EC) Setpoint' into cells H9-H20. Should be 1700 us/cm unless otherwise noted.
(Please note: The calculations in this spreadsheet are locked and cannot be altered)

## 3.6 Audit Checklist
3.6 Cooling Tower Water Audit Checklist
The overall water efficiency of a cooling tower system should be regularly reviewed and optimised where possible to ensure good overall management. This audit or review process can be used
during normal operating scenario's or used as a troubleshooting tool when issues have been flagged and investigation is required.
The following checklist outlines the major areas that should be reviewed during an audit process.
It should be noted that this checklist is not a comprehensive list but includes sufficient information to undertaken a medium level of review.
If issues are identified during the audit process or the audit process does not provide enough detail for troubleshooting purposes then the further investigation by competent persons would
be required.
Cooling Tower System Name:
Cooling Tower System Location:
Audit Date:
Audit Completed By:
Reason for Audit:
Area: | Review Area: | Items | Audit Comments
Cooling Tower: | Air Inlet: | Check for any obstructions or contamination. Assess for short circuiting of discharge air.
| Casing: | Check for any evidence of splashing, leaks or damage around tower
| Fill Pack: | Check for any evidence of blockages, damage or contamination
| Drift Eliminators: | Check for any evidence of blockages, damage or drift
| Water Distribution: | Check for poor distribution or blockages
| Fan: | Check for any evidence of malfunction, poor control or damage
| Level Control: | Check basin level control and operation of makeup control mechanism.
Ancillary Equipment: | Pumps: | Check for any evidence of leaking pumps
| Filters: | Check for any evidence of filter failure, blockage or leaks/bypassing
| Pipework: | Check for any evidence of leaking pipework or damage
| Valves: | Check for any evidence of leaking valves or damage
Water Meters: | Inlet Water Meter: | Check operation and functionality of inlet water meter/s
| Bleed Water Meter: | Check operation and functionality of bleed water meter/s
Water Treatment: | Control Equipment: | Check functionality and operational setpoints of bleed control system.
Check functionality and operational setpoints of water treatment control equipment.
| Water Quality | Check pH, conductivity and temperature of cooling tower water
Check pH and conductivity of mains water

## C.7 Water Efficiency Ratio
3.7 Cooling Tower Water Efficiency Ratio
Documenting and understanding historical cooling tower water consumption is a vital component of a best practice water efficiency program.
Understanding and tracking cooling tower water consumption trends, both historical and current, allows better overall monitoring and control.
This table allows a basic overview of cooling tower water consumption to be monitored and evaluated to ensure a basic level of understanding.
Site Name:
Description | Details
System Identification | Main Cooling Tower System
Water Meter Identification Number | ABC 12345 |  | ABC 54321
| Monthly Water Consumption (kL) | Average System Heat Load (kW) | Water Efficiency Ratio (kL/kW)
January | 481.0865 | 607.4053 | 0.79204
February | 550.9537 | 684.3008 | 0.80513
March | 506.4578 | 666.7742 | 0.75956
April | 340.4867 | 456.9355 | 0.74515
May | 249.8643 | 326.8065 | 0.76456
June
July
August
September
October
November
December
AVERAGE | 425.7698 | 548.4444 | 0.77329
Maximum Desired Efficiency Ratio (kL/kW) |  |  | 0.9

## C.7 Action Plan
C.6 Cooling Tower Opportunity Action Plan.
The cooling tower water efficiency opportunity Action Plan is a document that will assist you in documenting recommended
water saving actions and allocating desired outcomes and allocating tasks to the responsible stakeholder.
It allows formal tracking of progress and allows management to easily review and track status of tasks being implemented.
Item No. | Action | Desired Outcome | Responsible Party | Date By | Status | Actual outcome